## Summary
O&M KPI pack - Hill of Towie (21 x Siemens SWT-2.3-VS-82) - 2021-11
Working material generated from the event log; definitions in the sheet notes.
KPI | Value
Farm | Hill of Towie (21 x Siemens SWT-2.3-VS-82)
Month | 2021-11
Time zone | UTC
Turbines | 21
Hours in month | 720
Failures (month) | 10
Failures (12 months) | 201
Failures per turbine-year (12 months) | 10.2349
MTBF h (12 months) | 856.4823
MTTR h (month) | 20.5067
MTTR h (12 months) | 31.8653
Failure downtime h (month) | 205.0667
Repeat failures (month) | 1
Repeat rate (12 months) | 43.28%
Auto resets share (month) | 30%
Median on-site response h (12 months)
Codes making 80 % of downtime (month) | 5
Bad-actor turbines (12 months) | T06, T19
Crow-AMSAA beta (to month end) | 1.0371
Reliability trend | no significant trend
Stop h: forced_outage | 631.5192
Stop h: environmental | 62.7769
Stop h: technical_standby | 8.2922
Stop h: unknown | 401.165
Lost MWh (month, all stops) | 920.0229
Lost MWh: forced_outage | 534.0427
Lost MWh: environmental | 55.7004
Lost MWh: technical_standby | 2.0214
Lost MWh: unknown | 328.2583

## Pareto codes
Attributed stop hours (first-up rule, no double counting), all categories; rows inside 80 % cumulative share are the vital few.
code | description | component | hours | share | cum_share | lost_mwh | stops | first_up | failures
3413 |  | unmapped | 515.8964 | 46.74% | 46.74% | 393.421 | 1 | 0 | 0
1020 |  | unmapped | 213.8981 | 19.38% | 66.12% | 128.4863 | 46 | 22 | 0
1025 |  | unmapped | 92.7069 | 8.399% | 74.52% | 91.5942 | 2 | 0 | 0
1015 |  | unmapped | 48.9242 | 4.433% | 78.95% | 38.0697 | 9 | 0 | 0
8230 |  | environment | 43.2267 | 3.916% | 82.87% | 18.9038 | 2 | 2 | 0
63016 |  | unmapped | 37.1617 | 3.367% | 86.23% | 33.5428 | 4 | 2 | 2
10128 |  | unmapped | 28.5875 | 2.59% | 88.82% | 36.8328 | 8 | 0 | 2
8000 |  | environment | 19.5503 | 1.771% | 90.6% | 36.7967 | 50 | 34 | 0
7100 |  | unmapped | 15.1147 | 1.369% | 91.96% | 33.3296 | 3 | 1 | 0
6160 |  | unmapped | 14.7297 | 1.335% | 93.3% | 32.0842 | 2 | 1 | 1
8260 |  | unmapped | 12.9106 | 1.17% | 94.47% | 26.7856 | 33 | 7 | 0
3220 |  | unmapped | 12.2372 | 1.109% | 95.58% | 28.0927 | 1 | 0 | 1
13225 |  | unmapped | 10.4419 | 0.946% | 96.52% | 0.84749 | 1 | 0 | 0
1110 |  | unmapped | 9.5286 | 0.8633% | 97.39% | 5.1992 | 1 | 1 | 0
13172 |  | unmapped | 8.8589 | 0.8026% | 98.19% | 5.651 | 0 | 0 | 0
3130 |  | pitch | 4.8922 | 0.4432% | 98.63% | 1.7235 | 120 | 96 | 0
10105 |  | yaw | 3.4 | 0.308% | 98.94% | 0.29789 | 26 | 22 | 0
1001 |  | unmapped | 2.9319 | 0.2656% | 99.21% | 3.2554 | 43 | 1 | 0
8110 |  | unmapped | 2.8386 | 0.2572% | 99.46% | 0.25838 | 34 | 32 | 0
1008 |  | unmapped | 2.015 | 0.1826% | 99.65% | 1.2255 | 4 | 3 | 0
10118 |  | unmapped | 1.8972 | 0.1719% | 99.82% | 0.9452 | 61 | 1 | 0
3172 |  | unmapped | 1.1303 | 0.1024% | 99.92% | 1.5171 | 25 | 0 | 1
13902 |  | unmapped | 0.47667 | 0.04319% | 99.96% | 1.0957 | 23 | 2 | 3
9304 |  | unmapped | 0.2775 | 0.02514% | 99.99% | 0.033742 | 6 | 0 | 0
3412 |  | unmapped | 0.10167 | 0.009211% | 100% | 0.012628 | 2 | 0 | 0
1023 |  | unmapped | 0.010556 | 0.0009563% | 100% | 0.014413 | 29 | 0 | 0
1024 |  | unmapped | 0.0072222 | 0.0006543% | 100% | 0.0042481 | 17 | 0 | 0
14001 |  | unmapped | 0.00083333 | 7.55e-05% | 100% | 0.0019155 | 33 | 0 | 0
1022 |  | unmapped | 0.00027778 | 2.517e-05% | 100% | 3.9781e-05 | 3 | 0 | 0
1005 |  | environment | 0 | 0% | 100% | 0 | 62 | 0 | 0
7111 |  | unmapped | 0 | 0% | 100% | 0 | 34 | 0 | 0
15001 |  | unmapped | 0 | 0% | 100% | 0 | 33 | 0 | 0
3171 |  | unmapped | 0 | 0% | 100% | 0 | 24 | 0 | 0
3173 |  | unmapped | 0 | 0% | 100% | 0 | 22 | 0 | 0
5104 |  | unmapped | 0 | 0% | 100% | 0 | 21 | 0 | 0
5110 |  | unmapped | 0 | 0% | 100% | 0 | 21 | 0 | 0
5111 |  | unmapped | 0 | 0% | 100% | 0 | 21 | 0 | 0
1018 |  | unmapped | 0 | 0% | 100% | 0 | 20 | 0 | 0
5201 |  | unmapped | 0 | 0% | 100% | 0 | 20 | 0 | 0
1003 |  | unmapped | 0 | 0% | 100% | 0 | 19 | 0 | 0
5112 |  | unmapped | 0 | 0% | 100% | 0 | 17 | 0 | 0
13325 |  | unmapped | 0 | 0% | 100% | 0 | 12 | 0 | 0
2700 |  | unmapped | 0 | 0% | 100% | 0 | 12 | 0 | 0
13900 |  | unmapped | 0 | 0% | 100% | 0 | 11 | 0 | 0
10200 |  | unmapped | 0 | 0% | 100% | 0 | 8 | 0 | 0
9111 |  | unmapped | 0 | 0% | 100% | 0 | 8 | 0 | 0
2200 |  | unmapped | 0 | 0% | 100% | 0 | 7 | 0 | 0
5113 |  | unmapped | 0 | 0% | 100% | 0 | 6 | 0 | 0
5200 |  | unmapped | 0 | 0% | 100% | 0 | 4 | 0 | 0
63027 |  | unmapped | 0 | 0% | 100% | 0 | 4 | 0 | 0
9303 |  | unmapped | 0 | 0% | 100% | 0 | 4 | 0 | 0
9306 |  | unmapped | 0 | 0% | 100% | 0 | 3 | 0 | 0
3128 |  | unmapped | 0 | 0% | 100% | 0 | 1 | 0 | 0
3219 |  | unmapped | 0 | 0% | 100% | 0 | 1 | 0 | 0
3411 |  | unmapped | 0 | 0% | 100% | 0 | 1 | 0 | 0
6102 |  | unmapped | 0 | 0% | 100% | 0 | 1 | 0 | 0
63003 |  | unmapped | 0 | 0% | 100% | 0 | 1 | 0 | 0

## Pareto components
The same grouped by component (code mapping).
component | hours | share | cum_share | lost_mwh | stops | first_up | failures
unmapped | 1032.6842 | 93.56% | 93.56% | 862.301 | 727 | 73 | 10
environment | 62.7769 | 5.688% | 99.25% | 55.7004 | 114 | 36 | 0
pitch | 4.8922 | 0.4432% | 99.69% | 1.7235 | 120 | 96 | 0
yaw | 3.4 | 0.308% | 100% | 0.29789 | 26 | 22 | 0

## MTBF turbines
Failure episodes (forced outage, not fleet-wide). MTBF = operating hours / failures, 90 % chi-square interval. MTTR = mean time to restore (first stop to restart).
turbine_id | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
T06 | 76 | 6527.7297 | 85.8912 | 70.9695 | 104.8613 | 102.0594 | 29.1013 | 1.0728 | 8.7237 | 2211.7
T20 | 6 | 6823.4183 | 1137.2364 | 576.1856 | 2611.3203 | 7.7082 | 277.8786 | 9.3278 | 823.6771 | 1667.2717
T18 | 8 | 8089.9236 | 1011.2405 | 560.4517 | 2032.224 | 8.6686 | 76.1377 | 11.8578 | 188.2931 | 609.1014
T03 | 10 | 7991.6986 | 799.1699 | 471.147 | 1473.014 | 10.9689 | 36.7386 | 10.6169 | 112.0853 | 367.3858
T04 | 4 | 8451.1433 | 2112.7858 | 923.2671 | 6185.3396 | 4.149 | 54.8538 | 19.8968 | 133.8112 | 219.4153
T21 | 5 | 8294.5406 | 1658.9081 | 788.9768 | 4210.107 | 5.2842 | 42.2663 | 36.6111 | 90.2743 | 211.3314
T07 | 6 | 8194.1103 | 1365.685 | 691.9301 | 3135.8837 | 6.4188 | 33.9325 | 18.9301 | 82.7347 | 203.595
T05 | 7 | 8252.3633 | 1178.909 | 627.6462 | 2511.8936 | 7.4357 | 21.992 | 6.0603 | 66.3218 | 153.9442
T01 | 5 | 8126.8469 | 1625.3694 | 773.0258 | 4124.9898 | 5.3932 | 29.9719 | 20.9417 | 67.1758 | 149.8597
T12 | 5 | 8494.5872 | 1698.9174 | 808.0052 | 4311.6459 | 5.1598 | 29.4622 | 16.1561 | 64.2599 | 147.3108
T11 | 4 | 8457.9881 | 2114.497 | 924.0149 | 6190.3492 | 4.1457 | 24.118 | 18.3086 | 47.9217 | 96.4719
T08 | 9 | 8122.0136 | 902.446 | 517.1539 | 1729.8445 | 9.7136 | 8.9689 | 0.096944 | 22.4859 | 80.7203
T19 | 29 | 8249.0511 | 284.45 | 208.6203 | 397.6217 | 30.8174 | 2.3192 | 0.025833 | 5.1982 | 67.2558
T02 | 4 | 8628.9892 | 2157.2473 | 942.6964 | 6315.5039 | 4.0635 | 15.6008 | 6.786 | 36.6829 | 62.4033
T14 | 6 | 8402.1175 | 1400.3529 | 709.4947 | 3215.488 | 6.2599 | 9.1973 | 2.0772 | 25.4492 | 55.1836
T16 | 5 | 8260.3111 | 1652.0622 | 785.7209 | 4192.733 | 5.3061 | 10.4425 | 1.9453 | 26.2076 | 52.2125
T09 | 3 | 8609.3669 | 2869.789 | 1110.3622 | 10528.87 | 3.0546 | 11.8481 | 0.30306 | 28.1764 | 35.5442
T17 | 3 | 8432.0031 | 2810.6677 | 1087.4873 | 10311.9619 | 3.1188 | 3.6208 | 3.6311 | 6.4313 | 10.8625
T15 | 3 | 8657.2131 | 2885.7377 | 1116.533 | 10587.3836 | 3.0377 | 1.0385 | 0.089444 | 2.4181 | 3.1156
T10 | 2 | 8590.3772 | 4295.1886 | 1364.463 | 24173.6287 | 2.0409 | 0.069028 | 0.069028 | 0.10003 | 0.13806
T13 | 1 | 8497.1406 | 8497.1406 | 1791.1853 | 165657.9219 | 1.0316 | 0.10028 | 0.10028 | 0.10028 | 0.10028

## MTBF components
Operating hours of the whole fleet per component.
component | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
unmapped | 201 | 172152.9333 | 856.4823 | 761.9668 | 965.7278 | 10.2349 | 31.8653 | 1.0869 | 54.0881 | 6404.9233

## Bad actors
One-sided exact Poisson test against the fleet rate, Benjamini-Hochberg q < 0.05.
turbine_id | failures | expected | ratio | p | q | failure_downtime_h | downtime_vs_median | bad_actor | table | code | fleet_failures
T06 | 76 | 7.6216 | 9.9717 | 3.1268e-48 | 6.5663e-47 | 2211.7 | 22.9258 | TRUE | turbine vs fleet rate
T19 | 29 | 9.6313 | 3.011 | 3.6539e-07 | 3.8366e-06 | 67.2558 | 0.69715 | TRUE | turbine vs fleet rate
T03 | 10 | 9.3308 | 1.0717 | 0.4561 | 0.99995 | 367.3858 | 3.8082 | FALSE | turbine vs fleet rate
T08 | 9 | 9.483 | 0.94907 | 0.60608 | 0.99995 | 80.7203 | 0.83672 | FALSE | turbine vs fleet rate
T18 | 8 | 9.4455 | 0.84696 | 0.72565 | 0.99995 | 609.1014 | 6.3138 | FALSE | turbine vs fleet rate
T20 | 6 | 7.9668 | 0.75313 | 0.8057 | 0.99995 | 1667.2717 | 17.2825 | FALSE | turbine vs fleet rate
T05 | 7 | 9.6352 | 0.7265 | 0.84513 | 0.99995 | 153.9442 | 1.5957 | FALSE | turbine vs fleet rate
T07 | 6 | 9.5672 | 0.62714 | 0.91466 | 0.99995 | 203.595 | 2.1104 | FALSE | turbine vs fleet rate
T14 | 6 | 9.81 | 0.61162 | 0.92538 | 0.99995 | 55.1836 | 0.57202 | FALSE | turbine vs fleet rate
T01 | 5 | 9.4886 | 0.52695 | 0.95945 | 0.99995 | 149.8597 | 1.5534 | FALSE | turbine vs fleet rate
T16 | 5 | 9.6445 | 0.51843 | 0.96326 | 0.99995 | 52.2125 | 0.54122 | FALSE | turbine vs fleet rate
T21 | 5 | 9.6844 | 0.51629 | 0.96418 | 0.99995 | 211.3314 | 2.1906 | FALSE | turbine vs fleet rate
T12 | 5 | 9.918 | 0.50413 | 0.96916 | 0.99995 | 147.3108 | 1.527 | FALSE | turbine vs fleet rate
T04 | 4 | 9.8673 | 0.40538 | 0.98861 | 0.99995 | 219.4153 | 2.2744 | FALSE | turbine vs fleet rate
T11 | 4 | 9.8753 | 0.40505 | 0.98868 | 0.99995 | 96.4719 | 1 | FALSE | turbine vs fleet rate
T02 | 4 | 10.0749 | 0.39703 | 0.99022 | 0.99995 | 62.4033 | 0.64685 | FALSE | turbine vs fleet rate
T17 | 3 | 9.8449 | 0.30473 | 0.99686 | 0.99995 | 10.8625 | 0.1126 | FALSE | turbine vs fleet rate
T09 | 3 | 10.052 | 0.29845 | 0.99735 | 0.99995 | 35.5442 | 0.36844 | FALSE | turbine vs fleet rate
T15 | 3 | 10.1079 | 0.2968 | 0.99747 | 0.99995 | 3.1156 | 0.032295 | FALSE | turbine vs fleet rate
T10 | 2 | 10.0298 | 0.19941 | 0.99951 | 0.99995 | 0.13806 | 0.001431 | FALSE | turbine vs fleet rate
T13 | 1 | 9.921 | 0.1008 | 0.99995 | 0.99995 | 0.10028 | 0.0010395 | FALSE | turbine vs fleet rate
T06 | 57 | 2.313 | 24.6432 | 1.4572e-57 | 1.224e-55 |  |  | TRUE | code on one turbine | 3220 | 61
T19 | 22 | 2.7313 | 8.0549 | 2.6161e-13 | 1.0988e-11 |  |  | TRUE | code on one turbine | 13902 | 57
T06 | 6 | 0.26543 | 22.6051 | 3.8706e-07 | 1.0838e-05 |  |  | TRUE | code on one turbine | 3123 | 7
T06 | 4 | 0.15167 | 26.3726 | 1.9537e-05 | 0.00032822 |  |  | TRUE | code on one turbine | 3125 | 4
T06 | 5 | 0.30335 | 16.4828 | 1.6639e-05 | 0.00032822 |  |  | TRUE | code on one turbine | 3173 | 8
T20 | 4 | 0.27745 | 14.417 | 0.00019796 | 0.0027715 |  |  | TRUE | code on one turbine | 13172 | 7
T05 | 3 | 0.23968 | 12.5166 | 0.0019194 | 0.023032 |  |  | TRUE | code on one turbine | 3172 | 5

## Jack-knife codes
Knights' jack-knife: failures vs mean restore time; limits = mean failures per code and the overall MTTR.
code | failures | mttr_h | downtime_h | quadrant | n_limit | mttr_limit_h
3413 | 5 | 381.2895 | 1906.4475 | acute | 6.7 | 31.8653
63026 | 1 | 1627.2792 | 1627.2792 | acute | 6.7 | 31.8653
13110 | 4 | 189.7726 | 759.0903 | acute | 6.7 | 31.8653
64066 | 5 | 80.3122 | 401.5611 | acute | 6.7 | 31.8653
13900 | 1 | 179.5244 | 179.5244 | acute | 6.7 | 31.8653
3220 | 61 | 2.839 | 173.1811 | chronic | 6.7 | 31.8653
3172 | 5 | 29.9732 | 149.8658 | ok | 6.7 | 31.8653
13225 | 2 | 74.3771 | 148.7542 | acute | 6.7 | 31.8653
3125 | 4 | 36.6652 | 146.6608 | acute | 6.7 | 31.8653
10128 | 5 | 27.7807 | 138.9036 | ok | 6.7 | 31.8653
63036 | 4 | 32.514 | 130.0558 | acute | 6.7 | 31.8653
13902 | 57 | 1.5978 | 91.0728 | chronic | 6.7 | 31.8653
3173 | 8 | 9.9877 | 79.9017 | chronic | 6.7 | 31.8653
3123 | 7 | 11.2656 | 78.8589 | chronic | 6.7 | 31.8653
63016 | 5 | 12.6438 | 63.2189 | ok | 6.7 | 31.8653
13172 | 7 | 8.9708 | 62.7958 | chronic | 6.7 | 31.8653
9306 | 1 | 47.3425 | 47.3425 | acute | 6.7 | 31.8653
13309 | 1 | 44.6375 | 44.6375 | acute | 6.7 | 31.8653
15037 | 1 | 33.7556 | 33.7556 | acute | 6.7 | 31.8653
3412 | 3 | 10.1902 | 30.5706 | ok | 6.7 | 31.8653
14038 | 2 | 12.3788 | 24.7575 | ok | 6.7 | 31.8653
3171 | 1 | 23.5236 | 23.5236 | ok | 6.7 | 31.8653
4112 | 2 | 8.545 | 17.09 | ok | 6.7 | 31.8653
6160 | 1 | 15.1503 | 15.1503 | ok | 6.7 | 31.8653
3411 | 1 | 12.6467 | 12.6467 | ok | 6.7 | 31.8653
14042 | 1 | 8.1083 | 8.1083 | ok | 6.7 | 31.8653
15033 | 1 | 3.5808 | 3.5808 | ok | 6.7 | 31.8653
6102 | 2 | 1.6557 | 3.3114 | ok | 6.7 | 31.8653
14302 | 2 | 1.5549 | 3.1097 | ok | 6.7 | 31.8653
3126 | 1 | 0.16694 | 0.16694 | ok | 6.7 | 31.8653

## Repeats
The same code on the same turbine within 7 days after restart.
turbine_id | start | code | description | days_since_previous | chain_pos | duration_h
T07 | 2021-11-05 15:49 | 63016 |  | 0.044606 | 1 | 21.9089

## Repeat rate
chance_rate = repeat rate expected from the code's own frequency alone (Poisson).
code | failures | repeats | longest_chain | repeat_downtime_h | description | repeat_rate | chance_rate | excess
3220 | 61 | 44 | 11 | 138.4136 |  | 72.13% | 5.779% | 66.35%
13902 | 57 | 26 | 21 | 61.1561 |  | 45.61% | 5.411% | 40.2%
3123 | 7 | 5 | 6 | 71.1811 |  | 71.43% | 0.6808% | 70.75%
3173 | 8 | 3 | 4 | 14.0311 |  | 37.5% | 0.7777% | 36.72%
13172 | 7 | 3 | 4 | 21.3369 |  | 42.86% | 0.6808% | 42.18%
3125 | 4 | 2 | 3 | 84.1408 |  | 50% | 0.3896% | 49.61%
3172 | 5 | 1 | 2 | 69.0033 |  | 20% | 0.4867% | 19.51%
63016 | 5 | 1 | 2 | 21.9089 |  | 20% | 0.4867% | 19.51%
14302 | 2 | 1 | 2 | 1.6344 |  | 50% | 0.195% | 49.81%
4112 | 2 | 1 | 2 | 16.9072 |  | 50% | 0.195% | 49.81%
10128 | 5 | 0 | 1 | 0 |  | 0% | 0.4867% | -0.4867%
3413 | 5 | 0 | 1 | 0 |  | 0% | 0.4867% | -0.4867%
64066 | 5 | 0 | 1 | 0 |  | 0% | 0.4867% | -0.4867%
13110 | 4 | 0 | 1 | 0 |  | 0% | 0.3896% | -0.3896%
63036 | 4 | 0 | 1 | 0 |  | 0% | 0.3896% | -0.3896%
3412 | 3 | 0 | 1 | 0 |  | 0% | 0.2923% | -0.2923%
13225 | 2 | 0 | 1 | 0 |  | 0% | 0.195% | -0.195%
14038 | 2 | 0 | 1 | 0 |  | 0% | 0.195% | -0.195%
6102 | 2 | 0 | 1 | 0 |  | 0% | 0.195% | -0.195%
13309 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
13900 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
14042 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
15033 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
15037 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
3126 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
3171 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
3411 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
6160 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
63026 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%
9306 | 1 | 0 | 1 | 0 |  | 0% | 0.09754% | -0.09754%

## Cascades
Alarms starting within 2min after the first-up stop of an episode.
primary | primary_text | secondary | secondary_text | count | primary_episodes | confidence | lift
1020 |  | 1001 |  | 200 | 224 | 89.29% | 11.5556
1020 |  | 50000 |  | 167 | 224 | 74.55% | 11.4033
1020 |  | 1022 |  | 117 | 224 | 52.23% | 11.4316
1020 |  | 1005 |  | 79 | 224 | 35.27% | 11.3025
1020 |  | 1023 |  | 54 | 224 | 24.11% | 11.3853
1020 |  | 1024 |  | 52 | 224 | 23.21% | 11.5728
13902 |  | 14302 |  | 43 | 66 | 65.15% | 37.3166
13902 |  | 14038 |  | 27 | 66 | 40.91% | 39.3312
13902 |  | 5122 |  | 21 | 66 | 31.82% | 18.6206
13902 |  | 1018 |  | 19 | 66 | 28.79% | 19.871
13902 |  | 5104 |  | 19 | 66 | 28.79% | 17.2215
13902 |  | 5110 |  | 19 | 66 | 28.79% | 17.2215
13902 |  | 5111 |  | 19 | 66 | 28.79% | 17.6129
13902 |  | 5112 |  | 19 | 66 | 28.79% | 18.0226
13902 |  | 5201 |  | 19 | 66 | 28.79% | 25.8323
13902 |  | 15033 |  | 17 | 66 | 25.76% | 36.4944
13902 |  | 15324 |  | 16 | 66 | 24.24% | 34.3477
5201 |  | 1018 |  | 15 | 15 | 100% | 69.0256
5201 |  | 5104 |  | 15 | 15 | 100% | 59.8222
5201 |  | 5110 |  | 15 | 15 | 100% | 59.8222
5201 |  | 5111 |  | 15 | 15 | 100% | 61.1818
5201 |  | 5112 |  | 15 | 15 | 100% | 62.6047
13902 |  | 3173 |  | 15 | 66 | 22.73% | 21.0972
13902 |  | 3171 |  | 14 | 66 | 21.21% | 16.3152
13902 |  | 15038 |  | 13 | 66 | 19.7% | 37.8745
13902 |  | 3172 |  | 13 | 66 | 19.7% | 15.1498
5201 |  | 5122 |  | 12 | 15 | 80% | 46.8174
1008 |  | 1020 |  | 11 | 126 | 8.73% | 16.7868
1001 |  | 14147 |  | 8 | 18 | 44.44% | 92.0342
13902 |  | 13902 |  | 8 | 66 | 12.12% | 11.2518
13902 |  | 15042 |  | 8 | 66 | 12.12% | 32.6303
1008 |  | 1001 |  | 8 | 126 | 6.349% | 0.82173
1008 |  | 50000 |  | 8 | 126 | 6.349% | 0.97114
3220 |  | 13902 |  | 7 | 60 | 11.67% | 10.8299
3220 |  | 14001 |  | 7 | 60 | 11.67% | 24.159
3220 |  | 15001 |  | 7 | 60 | 11.67% | 22.4333
13902 |  | 15004 |  | 7 | 66 | 10.61% | 25.9559
1018 |  | 5104 |  | 6 | 6 | 100% | 59.8222
1018 |  | 5110 |  | 6 | 6 | 100% | 59.8222
1018 |  | 5111 |  | 6 | 6 | 100% | 61.1818

## Restoration
on_site / remote from the code roles; auto_reset = nothing logged and restored within 20min; response = failure start to first on-site event.
restoration | failures | restore_median_h | downtime_h | share | response_median_h | response_p90_h | window
auto_reset | 3 | 0.30306 | 0.64417 | 30% |  |  | month
not_logged | 7 | 20.3086 | 204.4225 | 70% |  |  | month
auto_reset | 58 | 0.081528 | 4.4686 | 28.86% |  |  | 12 months
not_logged | 143 | 2.4231 | 6400.4547 | 71.14% |  |  | 12 months

## Trend
Per local-time month.
period | failures | operating_h | mtbf_h | stop_h_environmental | stop_h_forced_outage | stop_h_technical_standby | stop_h_unknown | lost_mwh
2019-12 | 2 | 15594.8053 | 7797.4026 | 0 | 0.22167 | 8.7247 | 19.9836 | 0
2020-01 | 10 | 15303.0206 | 1530.3021 | 0 | 68.9861 | 5.5336 | 246.3119 | 0
2020-02 | 13 | 13074.8319 | 1005.7563 | 4.04 | 377.6544 | 9.0808 | 1150.0967 | 0
2020-03 | 33 | 14635.0203 | 443.4855 | 7.0175 | 77.4992 | 13.2636 | 889.9606 | 0
2020-04 | 7 | 13929.8406 | 1989.9772 | 0 | 62.9289 | 16.9928 | 1109.3389 | 0
2020-05 | 10 | 14544.6364 | 1454.4636 | 0 | 72.5961 | 31.4756 | 973.7381 | 0
2020-06 | 8 | 14587.1328 | 1823.3916 | 0 | 12.2681 | 21.4483 | 284.1581 | 0
2020-07 | 20 | 14860.7353 | 743.0368 | 0.017222 | 142.9881 | 17.3664 | 601.4042 | 0
2020-08 | 6 | 14805.9467 | 2467.6578 | 16.9358 | 46.8472 | 12.8953 | 740.7753 | 0
2020-09 | 10 | 14279.0642 | 1427.9064 | 720 | 24.5189 | 27.5125 | 67.4294 | 0
2020-10 | 7 | 14804.3689 | 2114.9098 | 636.1706 | 86.8139 | 11.9031 | 84.3994 | 0
2020-11 | 5 | 15013.47 | 3002.694 | 0 | 30.9142 | 8.6558 | 66.8578 | 0
2020-12 | 9 | 15245.0239 | 1693.8915 | 81.8392 | 95.74 | 11.6203 | 189.6128 | 0
2021-01 | 39 | 14927.0636 | 382.7452 | 346.3378 | 186.6361 | 8.5936 | 154.7169 | 420.8917
2021-02 | 20 | 13669.9167 | 683.4958 | 10.9075 | 196.1661 | 6.8969 | 227.3136 | 519.9621
2021-03 | 27 | 15030.2289 | 556.6751 | 0 | 535.6478 | 8.7164 | 48.7869 | 626.9159
2021-04 | 20 | 13363.5061 | 668.1753 | 22.0819 | 730.53 | 19.6556 | 983.1261 | 902.2065
2021-05 | 9 | 12198.9472 | 1355.4386 | 9.0842 | 14.6006 | 5.5917 | 543.3364 | 303.424
2021-06 | 17 | 14773.6667 | 869.0392 | 0 | 31.0492 | 21.3772 | 227.1881 | 105.2983
2021-07 | 8 | 15279.4189 | 1909.9274 | 0 | 98.6006 | 18.83 | 226.1697 | 47.7027
2021-08 | 14 | 15004.0792 | 1071.7199 | 0.086111 | 155.255 | 93.7311 | 369.2306 | 69.4129
2021-09 | 16 | 14242.9769 | 890.1861 | 1.0008 | 53.4844 | 17.6272 | 804.0558 | 366.0745
2021-10 | 12 | 14403.7611 | 1200.3134 | 0.00055556 | 190.9139 | 7.5961 | 1021.4558 | 715.5973
2021-11 | 10 | 14014.3442 | 1401.4344 | 62.7769 | 631.5192 | 8.2922 | 401.165 | 920.0229

## Failures
Times in local time.
turbine_id | start | end | duration_h | code | description | component | first_code | n_events | restoration | response_h
T02 | 2021-11-09 14:45 | 2021-11-11 15:29 | 48.7319 | 10128 |  | unmapped | 10118 | 265 | not_logged
T07 | 2021-11-04 22:48 | 2021-11-05 14:45 | 15.9514 | 63016 |  | unmapped | 63016 | 26 | not_logged
T07 | 2021-11-05 15:49 | 2021-11-06 13:44 | 21.9089 | 63016 |  | unmapped | 63016 | 19 | not_logged
T09 | 2021-11-26 16:59 | 2021-11-26 17:18 | 0.30306 | 13902 |  | unmapped | 13902 | 5 | auto_reset
T11 | 2021-11-26 18:30 | 2021-11-27 14:48 | 20.3086 | 10128 |  | unmapped | 8000 | 33 | not_logged
T14 | 2021-11-26 17:00 | 2021-11-26 17:01 | 0.029722 | 13902 |  | unmapped | 13902 | 3 | auto_reset
T16 | 2021-11-26 17:40 | 2021-11-27 08:49 | 15.1503 | 6160 |  | unmapped | 6160 | 62 | not_logged
T18 | 2021-11-26 16:55 | 2021-11-26 17:14 | 0.31139 | 13902 |  | unmapped | 8000 | 6 | auto_reset
T18 | 2021-11-26 19:12 | 2021-11-29 12:48 | 65.6153 | 3172 |  | unmapped | 7100 | 42 | not_logged
T20 | 2021-11-26 15:28 | 2021-11-27 08:13 | 16.7561 | 3220 |  | unmapped | 8000 | 15 | not_logged