## Summary
O&M KPI pack - Kelmarsh (6 x Senvion MM92) - 2021-03
Working material generated from the event log; definitions in the sheet notes.
KPI | Value
Farm | Kelmarsh (6 x Senvion MM92)
Month | 2021-03
Time zone | UTC
Turbines | 6
Hours in month | 744
Failures (month) | 7
Failures (12 months) | 27
Failures per turbine-year (12 months) | 4.8297
MTBF h (12 months) | 1815.0066
MTTR h (month) | 10.3266
MTTR h (12 months) | 34.3812
Failure downtime h (month) | 72.2864
Repeat failures (month) | 0
Repeat rate (12 months) | 7.407%
Auto resets share (month) | 42.86%
Median on-site response h (12 months) | 46.5919
Codes making 80 % of downtime (month) | 2
Bad-actor turbines (12 months) | none
Crow-AMSAA beta (to month end) | 0.85199
Reliability trend | improving
Stop h: forced_outage | 69.0253
Stop h: scheduled_maintenance | 144.8972
Stop h: technical_standby | 2.6544
Lost MWh (month, all stops) | 143.0074
Lost MWh: forced_outage | 58.5244
Lost MWh: scheduled_maintenance | 83.9439
Lost MWh: technical_standby | 0.53916

## Pareto codes
Attributed stop hours (first-up rule, no double counting), all categories; rows inside 80 % cumulative share are the vital few.
code | description | component | hours | share | cum_share | lost_mwh | stops | first_up | failures
20 | Manual stop - on site | service | 140.9167 | 65.07% | 65.07% | 82.9936 | 17 | 7 | 0
570 | Pitch too slow BP180 | pitch | 50.1386 | 23.15% | 88.22% | 53.1542 | 1 | 1 | 1
100 | Safety chain open | control | 17.7181 | 8.181% | 96.4% | 3.265 | 1 | 1 | 1
210 | Manual brake | service | 3.9806 | 1.838% | 98.23% | 0.95024 | 1 | 0 | 0
6200 | Cable autounwind | yaw | 1.0361 | 0.4784% | 98.71% | 0.058166 | 4 | 4 | 0
710 | Battery test | pitch | 0.95056 | 0.4389% | 99.15% | 0.42905 | 26 | 23 | 0
5760 | Hydraulic oil flushing operation | brake_hydraulics | 0.66778 | 0.3083% | 99.46% | 0.051947 | 4 | 4 | 0
4510 | Tower oscillation Y level 1 | tower_nacelle | 0.58167 | 0.2686% | 99.73% | 1.189 | 2 | 2 | 2
4540 | Tower oscillation X level 2 | tower_nacelle | 0.26056 | 0.1203% | 99.85% | 0.53451 | 1 | 1 | 1
4520 | Tower oscillation X level 1 | tower_nacelle | 0.1775 | 0.08196% | 99.93% | 0.36438 | 1 | 1 | 1
1620 | Implausible gear speed | gearbox | 0.14889 | 0.06875% | 100% | 0.017262 | 1 | 0 | 1

## Pareto components
The same grouped by component (code mapping).
component | hours | share | cum_share | lost_mwh | stops | first_up | failures
service | 144.8972 | 66.9% | 66.9% | 83.9439 | 18 | 7 | 0
pitch | 51.0892 | 23.59% | 90.49% | 53.5832 | 27 | 24 | 1
control | 17.7181 | 8.181% | 98.67% | 3.265 | 1 | 1 | 1
yaw | 1.0361 | 0.4784% | 99.15% | 0.058166 | 4 | 4 | 0
tower_nacelle | 1.0197 | 0.4708% | 99.62% | 2.0879 | 4 | 4 | 4
brake_hydraulics | 0.66778 | 0.3083% | 99.93% | 0.051947 | 4 | 4 | 0
gearbox | 0.14889 | 0.06875% | 100% | 0.017262 | 1 | 0 | 1

## MTBF turbines
Failure episodes (forced outage, not fleet-wide). MTBF = operating hours / failures, 90 % chi-square interval. MTTR = mean time to restore (first stop to restart).
turbine_id | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
T6 | 10 | 7860.4019 | 786.0402 | 463.4065 | 1448.8137 | 11.1521 | 74.1467 | 5.9097 | 97.6688 | 741.4672
T3 | 3 | 8300.5722 | 2766.8574 | 1070.5365 | 10151.2279 | 3.1682 | 17.3374 | 0.18 | 41.3598 | 52.0122
T4 | 3 | 8024.1167 | 2674.7056 | 1034.8816 | 9813.1351 | 3.2774 | 17.2599 | 0.26083 | 41.0588 | 51.7797
T5 | 2 | 8106.3167 | 4053.1583 | 1287.5766 | 22811.465 | 2.1628 | 25.4707 | 25.4707 | 45.6532 | 50.9414
T1 | 6 | 8261.7814 | 1376.9636 | 697.6444 | 3161.7814 | 6.3662 | 4.6577 | 0.29986 | 13.4951 | 27.9464
T2 | 3 | 8451.9889 | 2817.3296 | 1090.0649 | 10336.4037 | 3.1115 | 1.3819 | 1.2828 | 2.5363 | 4.1458

## MTBF components
Operating hours of the whole fleet per component.
component | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
drivetrain | 1 | 49005.1778 | 49005.1778 | 10330.2229 | 955391.5061 | 0.17888 | 677.7756 | 677.7756 | 677.7756 | 677.7756
converter | 2 | 49005.1778 | 24502.5889 | 7783.7967 | 137902.3229 | 0.35776 | 51.4565 | 51.4565 | 51.6151 | 102.9131
pitch | 3 | 49005.1778 | 16335.0593 | 6320.2668 | 59931.1366 | 0.53664 | 28.3981 | 33.2125 | 47.2016 | 85.1942
sensors | 4 | 49005.1778 | 12251.2944 | 5353.6981 | 35866.5871 | 0.71552 | 7.4192 | 7.1242 | 9.2494 | 29.6767
control | 1 | 49005.1778 | 49005.1778 | 10330.2229 | 955391.5061 | 0.17888 | 17.7181 | 17.7181 | 17.7181 | 17.7181
yaw | 2 | 49005.1778 | 24502.5889 | 7783.7967 | 137902.3229 | 0.35776 | 4.6842 | 4.6842 | 8.3546 | 9.3683
gearbox | 1 | 49005.1778 | 49005.1778 | 10330.2229 | 955391.5061 | 0.17888 | 2.8497 | 2.8497 | 2.8497 | 2.8497
tower_nacelle | 13 | 49005.1778 | 3769.6291 | 2371 | 6372.9344 | 2.3254 | 0.21517 | 0.2425 | 0.26283 | 2.7972

## Bad actors
One-sided exact Poisson test against the fleet rate, Benjamini-Hochberg q < 0.05.
turbine_id | failures | expected | ratio | p | q | failure_downtime_h | downtime_vs_median | bad_actor | table | code | fleet_failures
T6 | 10 | 4.3308 | 2.3091 | 0.013494 | 0.080964 | 741.4672 | 14.4365 | FALSE | turbine vs fleet rate
T1 | 6 | 4.5519 | 1.3181 | 0.30597 | 0.9179 | 27.9464 | 0.54412 | FALSE | turbine vs fleet rate
T4 | 3 | 4.421 | 0.67858 | 0.81734 | 0.93719 | 51.7797 | 1.0082 | FALSE | turbine vs fleet rate
T3 | 3 | 4.5733 | 0.65598 | 0.8345 | 0.93719 | 52.0122 | 1.0127 | FALSE | turbine vs fleet rate
T2 | 3 | 4.6567 | 0.64423 | 0.8433 | 0.93719 | 4.1458 | 0.08072 | FALSE | turbine vs fleet rate
T5 | 2 | 4.4663 | 0.4478 | 0.93719 | 0.93719 | 50.9414 | 0.99184 | FALSE | turbine vs fleet rate

## Jack-knife codes
Knights' jack-knife: failures vs mean restore time; limits = mean failures per code and the overall MTTR.
code | failures | mttr_h | downtime_h | quadrant | n_limit | mttr_limit_h
1055 | 1 | 677.7756 | 677.7756 | acute | 2.0769 | 34.3812
3110 | 2 | 51.4565 | 102.9131 | acute | 2.0769 | 34.3812
570 | 2 | 41.9557 | 83.9114 | acute | 2.0769 | 34.3812
3330 | 4 | 7.4192 | 29.6767 | chronic | 2.0769 | 34.3812
100 | 1 | 17.7181 | 17.7181 | ok | 2.0769 | 34.3812
6300 | 1 | 9.2722 | 9.2722 | ok | 2.0769 | 34.3812
1620 | 1 | 2.8497 | 2.8497 | ok | 2.0769 | 34.3812
4540 | 5 | 0.26111 | 1.3056 | chronic | 2.0769 | 34.3812
725 | 1 | 1.2828 | 1.2828 | ok | 2.0769 | 34.3812
4520 | 5 | 0.17933 | 0.89667 | chronic | 2.0769 | 34.3812
4510 | 2 | 0.29083 | 0.58167 | ok | 2.0769 | 34.3812
6120 | 1 | 0.096111 | 0.096111 | ok | 2.0769 | 34.3812
4500 | 1 | 0.013333 | 0.013333 | ok | 2.0769 | 34.3812

## Repeats
The same code on the same turbine within 7 days after restart.
turbine_id | start | code | description | days_since_previous | chain_pos | duration_h

## Repeat rate
chance_rate = repeat rate expected from the code's own frequency alone (Poisson).
code | failures | repeats | longest_chain | repeat_downtime_h | description | repeat_rate | chance_rate | excess
3330 | 4 | 2 | 3 | 13.8244 | 4-20mA conv. generator speed | 50% | 1.362% | 48.64%
4520 | 5 | 0 | 1 | 0 | Tower oscillation X level 1 | 0% | 1.699% | -1.699%
4540 | 5 | 0 | 1 | 0 | Tower oscillation X level 2 | 0% | 1.699% | -1.699%
3110 | 2 | 0 | 1 | 0 | Frequency converter error | 0% | 0.6833% | -0.6833%
4510 | 2 | 0 | 1 | 0 | Tower oscillation Y level 1 | 0% | 0.6833% | -0.6833%
570 | 2 | 0 | 1 | 0 | Pitch too slow BP180 | 0% | 0.6833% | -0.6833%
100 | 1 | 0 | 1 | 0 | Safety chain open | 0% | 0.3422% | -0.3422%
1055 | 1 | 0 | 1 | 0 | Max. drivetrain oscillations | 0% | 0.3422% | -0.3422%
1620 | 1 | 0 | 1 | 0 | Implausible gear speed | 0% | 0.3422% | -0.3422%
4500 | 1 | 0 | 1 | 0 | Tower resonance | 0% | 0.3422% | -0.3422%
6120 | 1 | 0 | 1 | 0 | Uncontrolled yaw movement | 0% | 0.3422% | -0.3422%
6300 | 1 | 0 | 1 | 0 | Yaw error | 0% | 0.3422% | -0.3422%
725 | 1 | 0 | 1 | 0 | Battery voltage axis 1 | 0% | 0.3422% | -0.3422%

## Cascades
Alarms starting within 2min after the first-up stop of an episode.
primary | primary_text | secondary | secondary_text | count | primary_episodes | confidence | lift
6690 | Icing (stop) | 6682 | Icing (dev. electr. power) | 4 | 4 | 100% | 124
3110 | Frequency converter error | 1050 | Drivetrain oscillations | 1 | 2 | 50% | 248

## Restoration
on_site / remote from the code roles; auto_reset = nothing logged and restored within 20min; response = failure start to first on-site event.
restoration | failures | restore_median_h | downtime_h | share | response_median_h | response_p90_h | window
auto_reset | 3 | 0.2425 | 0.68056 | 42.86% |  |  | month
on_site | 3 | 17.7181 | 71.2667 | 42.86% | 32.0482 | 43.6832 | month
not_logged | 1 | 0.33917 | 0.33917 | 14.29% |  |  | month
auto_reset | 13 | 0.18 | 2.5542 | 48.15% |  |  | 12 months
on_site | 9 | 33.2125 | 895.7228 | 33.33% | 46.5919 | 61.1944 | 12 months
not_logged | 5 | 6.1217 | 30.0158 | 18.52% |  |  | 12 months

## Trend
Per local-time month.
period | failures | operating_h | mtbf_h | stop_h_environmental | stop_h_forced_outage | stop_h_grid | stop_h_requested | stop_h_scheduled_maintenance | stop_h_technical_standby | lost_mwh
2019-04 | 1 | 4316.8386 | 4316.8386 | 0 | 0.18 | 0 | 0 | 0 | 2.9814 | 0.5776
2019-05 | 1 | 4053.9153 | 4053.9153 | 0 | 0.052778 | 0 | 0 | 14.3911 | 5.37 | 15.3084
2019-06 | 1 | 4282.5903 | 4282.5903 | 0 | 0.355 | 0 | 0 | 33.8828 | 3.0322 | 19.3252
2019-07 | 1 | 4419.8189 | 4419.8189 | 0 | 31.38 | 3.7111 | 0 | 0 | 9.0703 | 11.4896
2019-08 | 0 | 4441.8461 |  | 0.091667 | 0 | 0.34 | 0 | 17.1831 | 4.2497 | 3.9395
2019-09 | 1 | 4313.5128 | 4313.5128 | 0 | 0.55167 | 1.3506 | 0 | 0 | 4.585 | 1.0318
2019-10 | 1 | 4457.6781 | 4457.6781 | 0 | 0.26333 | 0.33972 | 0 | 1.6597 | 4.0592 | 1.1093
2019-11 | 9 | 4179.7494 | 464.4166 | 0 | 67.1822 | 44.4608 | 0 | 22.6017 | 4.6094 | 68.9324
2019-12 | 7 | 4260.1006 | 608.5858 | 0 | 7.0569 | 0 | 0 | 15.7744 | 4.9997 | 27.6618
2020-01 | 0 | 3990.3092 |  | 0 | 0 | 0.71833 | 0 | 10.0683 | 3.0311 | 11.672
2020-02 | 29 | 4056.9583 | 139.8951 | 0.044722 | 50.2886 | 0.16556 | 0 | 0 | 2.0092 | 104.077
2020-03 | 4 | 4376.9892 | 1094.2473 | 0 | 44.7569 | 0 | 0 | 2.1444 | 2.59 | 21.8461
2020-04 | 1 | 4313.0711 | 4313.0711 | 0 | 0.013333 | 0 | 0 | 0 | 6.9156 | 0.59951
2020-05 | 3 | 4417.1647 | 1472.3882 | 0 | 0.38083 | 0 | 0 | 38.7483 | 7.005 | 9.6026
2020-06 | 4 | 4096.1297 | 1024.0324 | 0 | 29.6767 | 31.2528 | 0 | 26.0103 | 4.3567 | 23.8254
2020-07 | 1 | 4397.4086 | 4397.4086 | 0.046389 | 1.3931 | 0 | 30.0933 | 21.7725 | 12.7344 | 9.6494
2020-08 | 4 | 4356.6908 | 1089.1727 | 0 | 57.5019 | 0 | 45.4153 | 0.63111 | 2.4994 | 105.7292
2020-09 | 0 | 4230.6819 |  | 0 | 36.4383 | 36.2367 | 13.1469 | 0 | 1.8758 | 11.9617
2020-10 | 1 | 4348.2358 | 4348.2358 | 0 | 51.2947 | 0.33667 | 0 | 0.63639 | 63.1331 | 129.3735
2020-11 | 1 | 4004.2072 | 4004.2072 | 0 | 0.17944 | 0 | 0 | 7.4919 | 87.6481 | 128.4793
2020-12 | 3 | 3436.2647 | 1145.4216 | 395.9611 | 0.78472 | 0 | 0 | 63.3786 | 2.0378 | 116.724
2021-01 | 1 | 4148.9367 | 4148.9367 | 261.3861 | 32.2367 | 0 | 0 | 18.3639 | 2.8214 | 144.7262
2021-02 | 1 | 3009.9306 | 3009.9306 | 64.1969 | 78.99 | 0.097778 | 43.155 | 490.0025 | 0.98278 | 432.6549
2021-03 | 7 | 4246.4558 | 606.6365 | 0 | 69.0253 | 0 | 0 | 144.8972 | 2.6544 | 143.0074

## Failures
Times in local time.
turbine_id | start | end | duration_h | code | description | component | first_code | n_events | restoration | response_h
T1 | 2021-03-07 23:30 | 2021-03-08 17:13 | 17.7181 | 100 | Safety chain open | control | 100 | 1 | on_site | 17.5044
T1 | 2021-03-11 05:59 | 2021-03-11 06:19 | 0.33917 | 4510 | Tower oscillation Y level 1 | tower_nacelle | 4510 | 1 | not_logged
T2 | 2021-03-09 08:29 | 2021-03-09 11:20 | 2.8497 | 1620 | Implausible gear speed | gearbox | 20 | 2 | on_site
T3 | 2021-03-11 02:56 | 2021-03-11 03:06 | 0.1775 | 4520 | Tower oscillation X level 1 | tower_nacelle | 4520 | 1 | auto_reset
T4 | 2021-03-11 02:20 | 2021-03-11 02:35 | 0.26056 | 4540 | Tower oscillation X level 2 | tower_nacelle | 4540 | 1 | auto_reset
T5 | 2021-03-11 05:07 | 2021-03-11 05:22 | 0.2425 | 4510 | Tower oscillation Y level 1 | tower_nacelle | 4510 | 1 | auto_reset
T5 | 2021-03-13 13:37 | 2021-03-15 16:19 | 50.6989 | 570 | Pitch too slow BP180 | pitch | 570 | 3 | on_site | 46.5919