## Summary
O&M KPI pack - Penmanshiel (14 x Senvion MM82) - 2020-11
Working material generated from the event log; definitions in the sheet notes.
KPI | Value
Farm | Penmanshiel (14 x Senvion MM82)
Month | 2020-11
Time zone | UTC
Turbines | 14
Hours in month | 720
Failures (month) | 4
Failures (12 months) | 281
Failures per turbine-year (12 months) | 21.6323
MTBF h (12 months) | 405.2272
MTTR h (month) | 14.1426
MTTR h (12 months) | 5.9454
Failure downtime h (month) | 56.5706
Repeat failures (month) | 0
Repeat rate (12 months) | 36.65%
Auto resets share (month) | 0%
Median on-site response h (12 months) | 13.9639
Codes making 80 % of downtime (month) | 4
Bad-actor turbines (12 months) | T02
Crow-AMSAA beta (to month end) | 0.88025
Reliability trend | improving
Stop h: forced_outage | 56.1683
Stop h: scheduled_maintenance | 8.8692
Stop h: environmental | 6.3353
Stop h: technical_standby | 6.9064
Lost MWh (month, all stops) | 103.5955
Lost MWh: forced_outage | 86.5306
Lost MWh: scheduled_maintenance | 3.1542
Lost MWh: environmental | 12.9735
Lost MWh: technical_standby | 0.93717

## Pareto codes
Attributed stop hours (first-up rule, no double counting), all categories; rows inside 80 % cumulative share are the vital few.
code | description | component | hours | share | cum_share | lost_mwh | stops | first_up | failures
100 | Safety chain open | control | 36.0167 | 46.01% | 46.01% | 59.9169 | 3 | 3 | 3
3000 | Frequency converter not ready | converter | 15.1483 | 19.35% | 65.36% | 25.4205 | 8 | 0 | 0
25 | Manual stop without login | service | 8.8692 | 11.33% | 76.69% | 3.1542 | 6 | 6 | 0
64 | Max. wind speed | environment | 6.3353 | 8.093% | 84.79% | 12.9735 | 20 | 14 | 0
715 | Charging circuit pitch | pitch | 5.0033 | 6.392% | 91.18% | 1.1932 | 1 | 1 | 1
6200 | Cable autounwind | yaw | 2.4089 | 3.077% | 94.25% | 0.032295 | 11 | 11 | 0
5760 | Hydraulic oil flushing operation | brake_hydraulics | 2.3369 | 2.985% | 97.24% | 0.051322 | 14 | 14 | 0
710 | Battery test | pitch | 2.1311 | 2.722% | 99.96% | 0.79511 | 55 | 53 | 0
707 | Stop battery test | pitch | 0.029444 | 0.03761% | 100% | 0.058446 | 1 | 1 | 0

## Pareto components
The same grouped by component (code mapping).
component | hours | share | cum_share | lost_mwh | stops | first_up | failures
control | 36.0167 | 46.01% | 46.01% | 59.9169 | 3 | 3 | 3
converter | 15.1483 | 19.35% | 65.36% | 25.4205 | 8 | 0 | 0
service | 8.8692 | 11.33% | 76.69% | 3.1542 | 6 | 6 | 0
pitch | 7.1639 | 9.152% | 85.84% | 2.0468 | 57 | 55 | 1
environment | 6.3353 | 8.093% | 93.94% | 12.9735 | 20 | 14 | 0
yaw | 2.4089 | 3.077% | 97.01% | 0.032295 | 11 | 11 | 0
brake_hydraulics | 2.3369 | 2.985% | 100% | 0.051322 | 14 | 14 | 0

## MTBF turbines
Failure episodes (forced outage, not fleet-wide). MTBF = operating hours / failures, 90 % chi-square interval. MTTR = mean time to restore (first stop to restart).
turbine_id | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
T02 | 46 | 7837.2694 | 170.3754 | 133.251 | 221.137 | 51.4511 | 8.6582 | 0.65139 | 15.0821 | 398.2789
T13 | 27 | 8112.7658 | 300.4728 | 217.885 | 425.6858 | 29.174 | 8.2335 | 0.49556 | 17.3987 | 222.305
T07 | 15 | 8046.5333 | 536.4356 | 348.3781 | 870.2407 | 16.3412 | 13.2904 | 3.3194 | 30.291 | 199.3553
T10 | 14 | 8045.7478 | 574.6963 | 367.6126 | 950.5916 | 15.2533 | 14.0716 | 0.64403 | 4.4269 | 197.0028
T15 | 28 | 8173.9886 | 291.9282 | 212.9258 | 410.74 | 30.0279 | 5.3736 | 0.60042 | 7.7576 | 150.4597
T14 | 10 | 8208.2686 | 820.8269 | 483.9148 | 1512.9318 | 10.6795 | 9.5898 | 0.79667 | 13.3106 | 95.8978
T12 | 22 | 8162.8292 | 371.0377 | 259.8402 | 548.0712 | 23.6256 | 3.875 | 1.5344 | 12.4227 | 85.2494
T11 | 25 | 8179.0403 | 327.1616 | 234.2485 | 470.5432 | 26.7941 | 3.1263 | 1.2611 | 5.7444 | 78.1586
T04 | 13 | 8110.6933 | 623.8995 | 392.4168 | 1054.7644 | 14.0503 | 4.6159 | 2.0044 | 8.7389 | 60.0061
T09 | 17 | 8211.9519 | 483.056 | 322.0471 | 758.1098 | 18.147 | 2.7044 | 0.9075 | 6.7544 | 45.975
T05 | 13 | 8188.0878 | 629.8529 | 396.1613 | 1064.8292 | 13.9175 | 2.9935 | 1.4072 | 8.6723 | 38.9158
T08 | 18 | 8232.7703 | 457.3761 | 308.4385 | 707.6289 | 19.1658 | 2.1533 | 0.60528 | 5.3404 | 38.7603
T01 | 18 | 8142.1039 | 452.3391 | 305.0417 | 699.8359 | 19.3793 | 1.9173 | 1.2015 | 4.0689 | 34.5114
T06 | 15 | 8216.7853 | 547.7857 | 355.7492 | 888.6536 | 16.0026 | 1.7194 | 0.90556 | 3.1384 | 25.7906

## MTBF components
Operating hours of the whole fleet per component.
component | failures | operating_h | mtbf_h | mtbf_lo_h | mtbf_hi_h | failures_per_turbine_year | mttr_h | ttr_median_h | ttr_p90_h | downtime_h
pitch | 20 | 113868.8356 | 5693.4418 | 3918.1323 | 8590.8584 | 1.5397 | 22.5212 | 1.0911 | 78.9576 | 450.4239
service | 43 | 113868.8356 | 2648.1125 | 2053.5777 | 3470.3794 | 3.3103 | 9.9765 | 3.0328 | 26.9566 | 428.9886
tower_nacelle | 130 | 113868.8356 | 875.9141 | 757.2206 | 1018.2201 | 10.0078 | 2.1281 | 0.93528 | 5.0844 | 276.6589
gearbox | 57 | 113868.8356 | 1997.6989 | 1602.2275 | 2520.5852 | 4.388 | 4.0602 | 0.030278 | 2.1368 | 231.4339
converter | 4 | 113868.8356 | 28467.2089 | 12439.8972 | 83339.8978 | 0.30793 | 30.8938 | 12.5596 | 75.7324 | 123.575
control | 16 | 113868.8356 | 7116.8022 | 4685.7321 | 11346.0867 | 1.2317 | 6.2461 | 0.79958 | 22.8133 | 99.9378
generator | 4 | 113868.8356 | 28467.2089 | 12439.8972 | 83339.8978 | 0.30793 | 11.1268 | 9.7547 | 19.2231 | 44.5072
electrical | 1 | 113868.8356 | 113868.8356 | 24003.3911 | 2219955.589 | 0.076983 | 6.8547 | 6.8547 | 6.8547 | 6.8547
operator | 1 | 113868.8356 | 113868.8356 | 24003.3911 | 2219955.589 | 0.076983 | 4.1883 | 4.1883 | 4.1883 | 4.1883
brake_hydraulics | 3 | 113868.8356 | 37956.2785 | 14685.8241 | 139256.4835 | 0.23095 | 1.3021 | 1.3817 | 1.8799 | 3.9064
yaw | 2 | 113868.8356 | 56934.4178 | 18086.4943 | 320430.9756 | 0.15397 | 0.095972 | 0.095972 | 0.096528 | 0.19194

## Bad actors
One-sided exact Poisson test against the fleet rate, Benjamini-Hochberg q < 0.05.
turbine_id | failures | expected | ratio | p | q | failure_downtime_h | downtime_vs_median | bad_actor | table | code | fleet_failures
T02 | 46 | 19.3404 | 2.3784 | 1.8348e-07 | 2.5687e-06 | 398.2789 | 4.8747 | TRUE | turbine vs fleet rate
T15 | 28 | 20.1714 | 1.3881 | 0.056966 | 0.36673 | 150.4597 | 1.8415 | FALSE | turbine vs fleet rate
T13 | 27 | 20.0203 | 1.3486 | 0.078585 | 0.36673 | 222.305 | 2.7209 | FALSE | turbine vs fleet rate
T11 | 25 | 20.1838 | 1.2386 | 0.16721 | 0.58522 | 78.1586 | 0.95661 | FALSE | turbine vs fleet rate
T12 | 22 | 20.1438 | 1.0921 | 0.36851 | 0.9957 | 85.2494 | 1.0434 | FALSE | turbine vs fleet rate
T01 | 18 | 20.0927 | 0.89585 | 0.70996 | 0.9957 | 34.5114 | 0.4224 | FALSE | turbine vs fleet rate
T08 | 18 | 20.3164 | 0.88598 | 0.72643 | 0.9957 | 38.7603 | 0.4744 | FALSE | turbine vs fleet rate
T09 | 17 | 20.2651 | 0.83888 | 0.79558 | 0.9957 | 45.975 | 0.5627 | FALSE | turbine vs fleet rate
T07 | 15 | 19.8568 | 0.75541 | 0.88947 | 0.9957 | 199.3553 | 2.44 | FALSE | turbine vs fleet rate
T06 | 15 | 20.277 | 0.73975 | 0.90543 | 0.9957 | 25.7906 | 0.31566 | FALSE | turbine vs fleet rate
T10 | 14 | 19.8549 | 0.70512 | 0.92984 | 0.9957 | 197.0028 | 2.4112 | FALSE | turbine vs fleet rate
T04 | 13 | 20.0152 | 0.64951 | 0.96125 | 0.9957 | 60.0061 | 0.73443 | FALSE | turbine vs fleet rate
T05 | 13 | 20.2062 | 0.64337 | 0.96448 | 0.9957 | 38.9158 | 0.4763 | FALSE | turbine vs fleet rate
T14 | 10 | 20.256 | 0.49368 | 0.9957 | 0.9957 | 95.8978 | 1.1737 | FALSE | turbine vs fleet rate
T02 | 9 | 0.68827 | 13.0762 | 5.1514e-08 | 4.8938e-06 |  |  | TRUE | code on one turbine | 715 | 10
T02 | 20 | 5.0932 | 3.9268 | 4.576e-07 | 2.1736e-05 |  |  | TRUE | code on one turbine | 4510 | 74
T15 | 7 | 0.86141 | 8.1262 | 3.3018e-05 | 0.0010456 |  |  | TRUE | code on one turbine | 455 | 12
T12 | 4 | 0.28674 | 13.9497 | 0.0002242 | 0.0053247 |  |  | TRUE | code on one turbine | 2810 | 4
T13 | 11 | 3.3486 | 3.285 | 0.00071731 | 0.013629 |  |  | TRUE | code on one turbine | 1550 | 47
T07 | 4 | 0.42399 | 9.4342 | 0.00096154 | 0.015224 |  |  | TRUE | code on one turbine | 1510 | 6
T15 | 3 | 0.21535 | 13.9306 | 0.0014175 | 0.019238 |  |  | TRUE | code on one turbine | 650 | 3
T11 | 10 | 3.3759 | 2.9621 | 0.002577 | 0.030602 |  |  | TRUE | code on one turbine | 1550 | 47

## Jack-knife codes
Knights' jack-knife: failures vs mean restore time; limits = mean failures per code and the overall MTTR.
code | failures | mttr_h | downtime_h | quadrant | n_limit | mttr_limit_h
21 | 43 | 9.9765 | 428.9886 | acute+chronic | 10.4074 | 5.9454
1550 | 47 | 4.6439 | 218.2653 | chronic | 10.4074 | 5.9454
550 | 2 | 97.0987 | 194.1975 | acute | 10.4074 | 5.9454
4510 | 74 | 1.824 | 134.9769 | chronic | 10.4074 | 5.9454
4530 | 46 | 2.7697 | 127.4072 | chronic | 10.4074 | 5.9454
3000 | 2 | 60.9851 | 121.9703 | acute | 10.4074 | 5.9454
715 | 10 | 9.9462 | 99.4617 | acute | 10.4074 | 5.9454
665 | 1 | 77.9839 | 77.9839 | acute | 10.4074 | 5.9454
100 | 4 | 19.4958 | 77.9831 | acute | 10.4074 | 5.9454
657 | 1 | 45.3406 | 45.3406 | acute | 10.4074 | 5.9454
2810 | 4 | 11.1268 | 44.5072 | acute | 10.4074 | 5.9454
658 | 1 | 28.5492 | 28.5492 | acute | 10.4074 | 5.9454
455 | 12 | 1.8296 | 21.9547 | chronic | 10.4074 | 5.9454
4540 | 6 | 1.1949 | 7.1692 | ok | 10.4074 | 5.9454
4520 | 4 | 1.7764 | 7.1056 | ok | 10.4074 | 5.9454
3410 | 1 | 6.8547 | 6.8547 | acute | 10.4074 | 5.9454
1510 | 6 | 1.1422 | 6.8533 | ok | 10.4074 | 5.9454
1620 | 3 | 1.5944 | 4.7833 | ok | 10.4074 | 5.9454
9210 | 1 | 4.1883 | 4.1883 | ok | 10.4074 | 5.9454
650 | 3 | 1.2902 | 3.8706 | ok | 10.4074 | 5.9454
305 | 1 | 2.0044 | 2.0044 | ok | 10.4074 | 5.9454
2100 | 2 | 0.95097 | 1.9019 | ok | 10.4074 | 5.9454
3110 | 2 | 0.80236 | 1.6047 | ok | 10.4074 | 5.9454
1800 | 1 | 1.5319 | 1.5319 | ok | 10.4074 | 5.9454
582 | 1 | 0.61111 | 0.61111 | ok | 10.4074 | 5.9454
725 | 1 | 0.40944 | 0.40944 | ok | 10.4074 | 5.9454
6120 | 2 | 0.095972 | 0.19194 | ok | 10.4074 | 5.9454

## Repeats
The same code on the same turbine within 7 days after restart.
turbine_id | start | code | description | days_since_previous | chain_pos | duration_h

## Repeat rate
chance_rate = repeat rate expected from the code's own frequency alone (Poisson).
code | failures | repeats | longest_chain | repeat_downtime_h | description | repeat_rate | chance_rate | excess
4510 | 74 | 32 | 7 | 58.8358 | Tower oscillation Y level 1 | 43.24% | 10.34% | 32.9%
1550 | 47 | 21 | 5 | 216.3489 | Missing gear oil (high rpm) | 44.68% | 6.699% | 37.98%
21 | 43 | 16 | 3 | 78.3139 | Manual stop - remote | 37.21% | 6.147% | 31.06%
4530 | 46 | 15 | 3 | 60.9406 | Tower oscillation Y level 2 | 32.61% | 6.562% | 26.05%
455 | 12 | 7 | 5 | 3.3619 | Repeating error BP52 | 58.33% | 1.755% | 56.58%
715 | 10 | 7 | 8 | 6.3186 | Charging circuit pitch | 70% | 1.465% | 68.54%
2810 | 4 | 2 | 3 | 19.5094 | Service generator brushes | 50% | 0.5884% | 49.41%
650 | 3 | 2 | 3 | 3.6997 | Pitch controller communication error | 66.67% | 0.4416% | 66.23%
1510 | 6 | 1 | 2 | 0.9875 | Low gearbox oil pressure | 16.67% | 0.8813% | 15.79%
4540 | 6 | 0 | 1 | 0 | Tower oscillation X level 2 | 0% | 0.8813% | -0.8813%
100 | 4 | 0 | 1 | 0 | Safety chain open | 0% | 0.5884% | -0.5884%
4520 | 4 | 0 | 1 | 0 | Tower oscillation X level 1 | 0% | 0.5884% | -0.5884%
1620 | 3 | 0 | 1 | 0 | Implausible gear speed | 0% | 0.4416% | -0.4416%
2100 | 2 | 0 | 1 | 0 | Feedback brake 1 | 0% | 0.2946% | -0.2946%
3000 | 2 | 0 | 1 | 0 | Frequency converter not ready | 0% | 0.2946% | -0.2946%
3110 | 2 | 0 | 1 | 0 | Frequency converter error | 0% | 0.2946% | -0.2946%
550 | 2 | 0 | 1 | 0 | Pitch current asymmetry | 0% | 0.2946% | -0.2946%
6120 | 2 | 0 | 1 | 0 | Uncontrolled yaw movement | 0% | 0.2946% | -0.2946%
1800 | 1 | 0 | 1 | 0 | Overload gear oil pump | 0% | 0.1474% | -0.1474%
305 | 1 | 0 | 1 | 0 | Brake control | 0% | 0.1474% | -0.1474%
3410 | 1 | 0 | 1 | 0 | UPS error | 0% | 0.1474% | -0.1474%
582 | 1 | 0 | 1 | 0 | Set point><actual value axis 2 | 0% | 0.1474% | -0.1474%
657 | 1 | 0 | 1 | 0 | Error pitch converter 2 | 0% | 0.1474% | -0.1474%
658 | 1 | 0 | 1 | 0 | Error pitch converter 3 | 0% | 0.1474% | -0.1474%
665 | 1 | 0 | 1 | 0 | Pitch error | 0% | 0.1474% | -0.1474%
725 | 1 | 0 | 1 | 0 | Battery voltage axis 1 | 0% | 0.1474% | -0.1474%
9210 | 1 | 0 | 1 | 0 | Externally stopped | 0% | 0.1474% | -0.1474%

## Cascades
Alarms starting within 2min after the first-up stop of an episode.
primary | primary_text | secondary | secondary_text | count | primary_episodes | confidence | lift
455 | Repeating error BP52 | 675 | Pitch measuring system 1><2 | 11 | 12 | 91.67% | 138.875
715 | Charging circuit pitch | 716 | Battery charge cycle axis 1 error | 7 | 10 | 70% | 181.8
715 | Charging circuit pitch | 717 | Battery charge cycle axis 2 error | 7 | 10 | 70% | 181.8
715 | Charging circuit pitch | 718 | Battery charge cycle axis 3 error | 7 | 10 | 70% | 181.8
64 | Max. wind speed | 4502 | Nat. tower freq. implausible | 2 | 739 | 0.2706% | 2.4601
582 | Set point><actual value axis 2 | 675 | Pitch measuring system 1><2 | 1 | 1 | 100% | 151.5
455 | Repeating error BP52 | 720 | Pitch batteries charging cycle | 1 | 12 | 8.333% | 151.5
710 | Battery test | 4607 | Heating/fan base box faulty | 1 | 539 | 0.1855% | 3.3729

## Restoration
on_site / remote from the code roles; auto_reset = nothing logged and restored within 20min; response = failure start to first on-site event.
restoration | failures | restore_median_h | downtime_h | share | response_median_h | response_p90_h | window
on_site | 1 | 5.1331 | 5.1331 | 25% |  |  | month
not_logged | 3 | 19.0811 | 51.4375 | 75% |  |  | month
auto_reset | 60 | 0.069306 | 7.0647 | 21.35% |  |  | 12 months
remote | 18 | 5.8411 | 332.8244 | 6.406% |  |  | 12 months
on_site | 46 | 3.7406 | 943.0636 | 16.37% | 13.9639 | 37.9186 | 12 months
not_logged | 157 | 1.1481 | 387.7139 | 55.87% |  |  | 12 months

## Trend
Per local-time month.
period | failures | operating_h | mtbf_h | stop_h_environmental | stop_h_forced_outage | stop_h_grid | stop_h_requested | stop_h_scheduled_maintenance | stop_h_technical_standby | stop_h_unknown | lost_mwh
2018-12 | 23 | 10264.1789 | 446.2686 | 28.5906 | 13.6189 | 0 | 0 | 98.5942 | 5.5939 | 0 | 121.8911
2019-01 | 33 | 10230.0269 | 310.0008 | 27.5033 | 74.9517 | 73.3211 | 0 | 3.4089 | 4.2344 | 0 | 0
2019-02 | 7 | 9381.8947 | 1340.2707 | 16.0083 | 1.8814 | 0 | 0 | 0 | 6.2542 | 0 | 0
2019-03 | 13 | 10221.8808 | 786.2985 | 15.5722 | 131.9772 | 0 | 0 | 36.8967 | 7.3875 | 0 | 0
2019-04 | 5 | 9950.6556 | 1990.1311 | 0.82861 | 25.1406 | 0 | 0 | 91.7847 | 10.9044 | 0 | 0
2019-05 | 2 | 10359.0336 | 5179.5168 | 0 | 17.0489 | 0.2 | 0 | 12.3683 | 27.0897 | 0 | 0
2019-06 | 9 | 9833.3242 | 1092.5916 | 0 | 53.6697 | 151.3864 | 0 | 33.8386 | 6.5769 | 0 | 0
2019-07 | 18 | 10111.9786 | 561.7766 | 0 | 24.8283 | 0 | 0 | 1.9856 | 14.8667 | 0 | 0
2019-08 | 6 | 9859.2978 | 1643.2163 | 0.092778 | 153.5928 | 394.2328 | 0 | 0.32778 | 4.5053 | 0 | 0
2019-09 | 7 | 9966.1425 | 1423.7346 | 0.046667 | 59.8256 | 0.37056 | 0 | 37.6333 | 15.5075 | 0 | 0
2019-10 | 28 | 10263.2119 | 366.5433 | 0.011944 | 53.4919 | 0.34194 | 0 | 55.3725 | 42.9622 | 0 | 0
2019-11 | 11 | 9542.2267 | 867.4752 | 0.79417 | 194.9044 | 0.033611 | 0 | 314.3942 | 24.6758 | 0 | 0
2019-12 | 12 | 10182.6994 | 848.5583 | 23.8222 | 5.5575 | 0 | 0 | 124.9336 | 6.0336 | 0 | 0
2020-01 | 52 | 10116.5686 | 194.5494 | 214.1856 | 53.8278 | 0 | 0 | 0.11056 | 5.8706 | 0 | 507.7457
2020-02 | 64 | 9268.9022 | 144.8266 | 176.6672 | 113.4478 | 0 | 0 | 132.1453 | 6.0464 | 0 | 630.5071
2020-03 | 6 | 10283.5378 | 1713.923 | 15.8769 | 2.2728 | 0 | 0 | 64.6475 | 47.9183 | 0 | 101.9404
2020-04 | 7 | 9916.4539 | 1416.6363 | 0.092222 | 92.3619 | 0 | 0 | 21.4558 | 48.6994 | 0 | 45.4107
2020-05 | 20 | 10288.1578 | 514.4079 | 39.9158 | 20.6039 | 0 | 0 | 41.0733 | 20.2822 | 0 | 113.1088
2020-06 | 33 | 8836.8747 | 267.7841 | 0.58889 | 1228.7725 | 0 | 0 | 1.0661 | 8.3103 | 0 | 141.8627
2020-07 | 4 | 10265.6533 | 2566.4133 | 0.046667 | 46.9594 | 0 | 0 | 5.0117 | 14.1442 | 0 | 27.9611
2020-08 | 14 | 10130.7281 | 723.6234 | 0 | 178.2608 | 0.029722 | 0 | 93.0147 | 12.99 | 0 | 131.8392
2020-09 | 43 | 7690.5408 | 178.8498 | 0 | 239.9128 | 17.9306 | 2032.2894 | 47.2906 | 8.6875 | 0 | 187.3517
2020-10 | 22 | 7016.4456 | 318.9293 | 4.2047 | 78.4664 | 0.056389 | 3234.5589 | 14.2572 | 2.1542 | 0 | 112.2086
2020-11 | 4 | 9872.2733 | 2468.0683 | 6.3353 | 56.1683 | 0 | 0 | 8.8692 | 6.9064 | 0 | 103.5955

## Failures
Times in local time.
turbine_id | start | end | duration_h | code | description | component | first_code | n_events | restoration | response_h
T02 | 2020-11-11 01:43 | 2020-11-11 20:48 | 19.0811 | 100 | Safety chain open | control | 100 | 5 | not_logged
T07 | 2020-11-18 00:46 | 2020-11-19 08:13 | 31.4522 | 100 | Safety chain open | control | 100 | 5 | not_logged
T08 | 2020-11-04 09:30 | 2020-11-04 14:38 | 5.1331 | 715 | Charging circuit pitch | pitch | 715 | 2 | on_site
T12 | 2020-11-08 23:20 | 2020-11-09 00:14 | 0.90417 | 100 | Safety chain open | control | 100 | 1 | not_logged